## Test Definitions (3)
|  |  | Row |  | Column (If no parameter listed, there is still a column generated with result(s) as defined in Test Result Format, but there is only one test parameter as defined in Row.) |  |  |  | Table (Generate the table as defined by Row/Column, and sweep through all combinations under Table) | [7 empty] | Test Result Format 1. If there are two results types listed, split the result column into two columns. (Two results per column.) 2. If Limit Type is not defined, then a Row Limit Type must be defined instead - A "Row Limit" is a limit applied to all test results in the row (One limit column per table) 3. If Limit Type is defined, then a Row Limit Type must not be defined - One limit column is created for each test result column. 4. If a Calc is defined, then a calculation is performed on the raw data, and the limit is applied to the calculated data, not the raw data | [9 empty] | Row Result/Limit Format 1. A Row Calc can be created to allow calculation based on the data in a row e.g. Avg efficiency is (1/lengthEff[x]) * (Eff[1] + Eff[2] + Eff[3] + Eff[4]) or in English, the sum of each efficiency point recorded, divided by the number of points recorded
Test Category |  | Test Item | Parameter | Array | Parameter #1 | Array #1 | Parameter #2 | Array #2 | Param. #1 | Array #1 | Param. #2 | Array #2 | Param. #3 | Array #3 | Param #4 | Array #4 | Result #1 Name | Result #1 Unit | Calc result #1 Name | Calc result #1 Unit | Limit #1 Type | Result #2 Name | Result #2 Unit | Calc result #2 Name | Calc result #2 Unit | Limit #2 Type | Row calc result #1 Name | Row calc result #1 Unit | Row limit #1 Type | Row calc result #2 Name | Row calc result #2 Unit | Row limit #2 Type
Input | TRUE | Input Current | V_in | 110, 240 | I_out | 50 | [10 empty] | I_in | A |  |  | max
| TRUE | No Load Input Power | V_in | 110, 240 | I_out | {I_out_P_nl} | [10 empty] | P_in | mW |  |  | max
| FALSE | Inrush Current | V_in | {V_in_I_inrush} | I_out | {I_out_I_inrush} | [10 empty] | I_pk | A |  |  | max
| FALSE | Efficiency | V_in | {V_in_eff} | I_out | {I_out_eff} | [10 empty] | Eff | % | [8 empty] | Avg Eff | % | min
| FALSE | Power Factor | V_in | {V_in_PF} | I_out | {I_out_PF} | [10 empty] | PF | % |  |  | min
Output | FALSE | Turn-on delay | V_in | {V_in_ton_delay} | I_out | {I_out_ton_delay} | [10 empty] | t_delay | s |  |  | max
| FALSE | Load Regulation | V_in | {V_in_loadreg} | I_out | {I_out_loadreg} | [10 empty] | v_out1_load | V |  |  |  | v_out2_load | V |  |  |  | load_reg | % | max
| FALSE | Line Regulation | I_out | {I_out_linereg} | V_in | {V_in_linereg} | [10 empty] | v_out1_line | V |  |  |  | v_out2_line | V |  |  |  | line_reg | % | max
| FALSE | Ripple | V_in | {V_in_ripple} | I_out | {I_out_ripple} | [10 empty] | v_ripple | mV | v_ripple_% | % | max
| FALSE | Transient Response - Load Step | V_in | {V_in_transresp} | ΔIout | {dI_out_transresp} | [10 empty] | v_max_dev_ls | V | v_max_dev_ls_% | % |  | t_recovery_ls | ms |  |  | max |  |  | max
| FALSE | Transient Response - Load Dump | V_in | {V_in_transresp} | ΔIout | {dI_out_transresp} | [10 empty] | v_max_dev_ld | V | v_max_dev_ld_% | % |  | t_recovery_ld | ms |  |  | max |  |  | max
|  | Startup Overshoot | V_in | {V_in_startupovsht} | I_out | {I_out_startupovsht} | [10 empty] | v_max_dev_so | V | v_max_dev_vo_% | % | max | [11 empty] | x
|  | Hold-up Time | V_in | {V_in_t_holdup} | I_out | {I_out_t_holdup} | [10 empty] | t_holdup | ms |  |  | min
Protections | FALSE | Input Under-Voltage | I_out | {I_out_Vin_uv} | [12 empty] | v_trip_uvp | Vac |  |  | max | v_restore_uvp | Vac |  |  | max
| FALSE | Output Over-Voltage | I_out | {I_out_Vout_ov} | V_in | {V_in_Vout_ov} | [10 empty] | v_trip_ovp | V | v_trip_ovp_% | % | min/max
| FALSE | Output Overcurrent | V_in | {V_in_ocp} | [12 empty] | I_trip_ocp | A | I_trip_ocp_% | % | min/max
| FALSE | Short Circuit | V_in | {V_in_scp} | [12 empty] | scp_passfail | (none) |  |  | pass/fail
|  | Over-Temperature | V_in | {V_in_otp} | I_out | {I_out_otp} | T_amb | {T_amb_otp} | [8 empty] | T_otp | °C |  |  | min/max
Safety |  | Dielectric Withstand | DW_cond | {DW_cond} | CFG_gnd | {g_cfg_x} | [10 empty] | dw_passfail | (none) |  |  | pass/fail
|  | Output Touch Current | Lk_cond | {Lk_cond_otc} | V_in | {V_in_otc} | CFG_gnd | {g_cfg_x} | [8 empty] | I_leak_ot | uA | [10 empty] | max
|  | Earth Leakage Current | Lk_cond | {Lk_cond_elc} | V_in | {V_in_elc} | CFG_gnd | {g_cfg_x} | [8 empty] | I_leak_el | uA | [10 empty] | max
EMC |  | Conducted Emissions | CE_freq_point | {ce_freq_point} |  |  |  |  | CFG_gnd | {g_cfg_x} | V_in | {V_in_ce} | I_out | {I_out_ce} | CE_L/N | {ce_cond} | ce_av_margin | dBuV |  |  | min | ce_qp_margin | dBuV |  |  | min
|  | Radiated Emissions | RE_freq_point | {ce_freq_point} |  |  |  |  | CFG_gnd | {g_cfg_x} | V_in | {V_in_re} | I_out | {I_out_re} | RE_H/V | {re_cond} | re_pk_margin | dBuV |  |  | min | re_qp_margin | dBuV |  |  | min
|  | Electrostatic Discharge (Air) | ESD_air_loc | {location_esda} | ESD_num_strikes | {Num_strikes_esd} | ESD_voltage | {v_esd_air} | V_in | {V_in_esd} | CFG_gnd | {g_cfg_x} |  |  |  |  | esd_air_criterion | A - D | [10 empty] | min (alphabetic)
| FALSE | Electrostatic Discharge (Contact) | ESD_cnct_loc | {location_esdc} | ESD_num_strikes | {Num_strikes_esd} | ESD_voltage | {v_esd_cnct} | V_in | {V_in_esd} | CFG_gnd | {g_cfg_x} |  |  |  |  | esd_cntc_criterion | A - D | [10 empty] | min (alphabetic)
|  | EFT/Burst | EFT_input_line | {input_line_EFT} | EFT_voltage | {v_eft} |  |  | V_in | {V_in_eft} | CFG_gnd | {g_cfg_x} |  |  |  |  | eft_ctriterion | A - D | [10 empty] | min (alphabetic)
| FALSE | Lightning Surge | Surge_input_line | {input_line_surge} | Surge_voltage | {v_surge} |  |  | V_in | {V_in_surge} | CFG_gnd | {g_cfg_x} |  |  |  |  | surge_criterion | A - D | [10 empty] | min (alphabetic)

## Sheet5
Row Conditions | Names | Units | Values
Example | V_in | *from cover page | *from cover page
Column Conditions | Names | Units | Values
Table Conditions | Names | Units | Values
Example | [Cfg_gnd, V_in, I_out] | [n/a, Vac, A] | [F1, F2], [120, 240], [50, 25]
Results | Name | Units
| Input Current | A
Specifications | Names | Units | Values | Connection | Type | P/F
|  |  |  | related to column, calculation, whole data | min/max/neither
Example |  |  |  | C1
Calculations | Names | Units | Equations | Connection
Partial or whole part of data
Pass/Fail | [7 empty] | TITLE
T_Name11 = T_Value11 (T_Unit11), T_Name12 = T_Value12 (T_Unit12)
[10 empty] | C_Name1 (C_Unit) |  |  |  |  | Spec_Name1 | C_Name2 (C_Unit) |  |  |  |  | Spec_Name1 |  | Spec_Name2
[10 empty] | C_VAL1 | C_VAL2 | C_VAL3 | C_VAL4 | Calc_Name1 | Spec_Unit1 | C_VAL1 | C_VAL2 | C_VAL3 | C_VAL4 | Calc_Name1 | Spec_Unit1 | Calc_Name2 | Spec_Unit2
[10 empty] | Result_Name (Result_Units) |  |  |  | Calc_Unit1 | Spec_Type1 | Result_Name (Result_Units) |  |  |  | Calc_Unit1 | Spec_Type1 | Calc_Unit2 | Spec_Type2
[8 empty] | R_Name (R_Unit) | R_VAL1 |  |  |  |  | f(x) | Spec_VAL11 |  |  |  |  | f(x) | Spec_VAL11 | f(x) | Spec_VAL21
[9 empty] | R_VAL2 |  |  |  |  | f(x) | Spec_VAL12 |  |  |  |  | f(x) | Spec_VAL12 | f(x) | Spec_VAL22
[9 empty] | R_VAL3 |  |  |  |  | f(x) | Spec_VAL13 |  |  |  |  | f(x) | Spec_VAL13 | f(x) | Spec_VAL23
[7 empty] | title | TITLE
[7 empty] | table cond | T_Name21 = T_Value21 (T_Unit21), T_Name22 = T_Value22 (T_Unit22)
[7 empty] | col/spec name |  |  | C_Name1 (C_Unit) |  |  |  |  | Spec_Name1 | C_Name2 (C_Unit) |  |  |  |  | Spec_Name1 |  | Spec_Name2
[10 empty] | C_VAL1 | C_VAL2 | C_VAL3 | C_VAL4 | Calc_Name1 | Spec_Unit1 | C_VAL1 | C_VAL2 | C_VAL3 | C_VAL4 | Calc_Name1 | Spec_Unit1 | Calc_Name2 | Spec_Unit2
[10 empty] | Result_Name (Result_Units) |  |  |  | Calc_Unit1 | Spec_Type1 | Result_Name (Result_Units) |  |  |  | Calc_Unit1 | Spec_Type1 | Calc_Unit2 | Spec_Type2
[8 empty] | R_Name (R_Unit) | R_VAL1 |  |  |  |  | f(x) | Spec_VAL11 |  |  |  |  | f(x) | Spec_VAL11 | f(x) | Spec_VAL21
[9 empty] | R_VAL2 |  |  |  |  | f(x) | Spec_VAL12 |  |  |  |  | f(x) | Spec_VAL12 | f(x) | Spec_VAL22
[9 empty] | R_VAL3 |  |  |  |  | f(x) | Spec_VAL13 |  |  |  |  | f(x) | Spec_VAL13 | f(x) | Spec_VAL23
TITLE
TC_Name21 = TC_Value21 (TC_Unit21), TC_Name22 = TC_Value22 (TC_Unit22)
[10 empty] | C_Name1 (C_Unit) |  |  |  | C_Name2 (C_Unit)
[10 empty] | C_VAL[1][1] | C_VAL[1][2] | C_VAL[1][3] | C_VAL[1][4] | C_VAL[2][1] | C_VAL[2][2] | C_VAL[2][3] | C_VAL[2][4]
[8 empty] | R_Name1 (R_Unit1) | R_VAL1
R_VAL2
R_VAL3
[8 empty] | R_Name2 (R_Unit2) | R_VAL1
R_VAL2
R_VAL3

## Cover Page
Product Information
Alias | Field | Value
GMN | Globtek Model Name
GPN | Globtek Product Number
CPN | Customer Product Number
General Specifications
Alias | Specification Name | Type | Value
vin_SL | Input Voltage | Specified Low | --
vin_NL | Input Voltage | Nominal Low | --
vin_NH | Input Voltage | Nominal High | --
vin_SH | Input Voltage | Specified High | --
Insert Sheet rows if needed….
iout_L | Output Current | low | --
iout_H | Output Current | high | --
Insert Sheet rows if needed….
gndCFG_F1 | Grounding Configuration | F1 | TRUE
gndCFG_F2 | Grounding Configuration | F2 | FALSE
gndCFG_F3 | Grounding Configuration | F3 | FALSE
Insert Sheet rows if needed….
num_out | Number of Outputs |  | 1

## Test Definitions
|  |  | Row |  | Column (If no parameter listed, there is still a column generated with result(s) as defined in Test Result Format, but there is only one test parameter as defined in Row.) |  |  |  | Table (Generate the table as defined by Row/Column, and sweep through all combinations under Table) | [7 empty] | Test Result Format 1. If there are two results types listed, split the result column into two columns. (Two results per column.) 2. If Limit Type is not defined, then a Row Limit Type must be defined instead - A "Row Limit" is a limit applied to all test results in the row (One limit column per table) 3. If Limit Type is defined, then a Row Limit Type must not be defined - One limit column is created for each test result column. 4. If a Calc is defined, then a calculation is performed on the raw data, and the limit is applied to the calculated data, not the raw data | [9 empty] | Row Result/Limit Format 1. A Row Calc can be created to allow calculation based on the data in a row e.g. Avg efficiency is (1/lengthEff[x]) * (Eff[1] + Eff[2] + Eff[3] + Eff[4]) or in English, the sum of each efficiency point recorded, divided by the number of points recorded
Test Category |  | Test Item | Parameter | Array | Parameter #1 | Array #1 | Parameter #2 | Array #2 | Param. #1 | Array #1 | Param. #2 | Array #2 | Param. #3 | Array #3 | Param #4 | Array #4 | Result #1 Name | Result #1 Unit | Calc result #1 Name | Calc result #1 Unit | Limit #1 Type | Result #2 Name | Result #2 Unit | Calc result #2 Name | Calc result #2 Unit | Limit #2 Type | Row calc result #1 Name | Row calc result #1 Unit | Row limit #1 Type | Row calc result #2 Name | Row calc result #2 Unit | Row limit #2 Type
Input | TRUE | Input Current | V_in | 110, 240 | I_out | 50 | [10 empty] | I_in | A |  |  | max
| TRUE | No Load Input Power | V_in | 110, 240 | I_out | {I_out_P_nl} | [10 empty] | P_in | mW |  |  | max
| FALSE | Inrush Current | V_in | {V_in_I_inrush} | I_out | {I_out_I_inrush} | [10 empty] | I_pk | A |  |  | max
| FALSE | Efficiency | V_in | {V_in_eff} | I_out | {I_out_eff} | [10 empty] | Eff | % | [8 empty] | Avg Eff | % | min
| FALSE | Power Factor | V_in | {V_in_PF} | I_out | {I_out_PF} | [10 empty] | PF | % |  |  | min
Output | FALSE | Turn-on delay | V_in | {V_in_ton_delay} | I_out | {I_out_ton_delay} | [10 empty] | t_delay | s |  |  | max
| FALSE | Load Regulation | V_in | {V_in_loadreg} | I_out | {I_out_loadreg} | [10 empty] | v_out1_load | V |  |  |  | v_out2_load | V |  |  |  | load_reg | % | max
| FALSE | Line Regulation | I_out | {I_out_linereg} | V_in | {V_in_linereg} | [10 empty] | v_out1_line | V |  |  |  | v_out2_line | V |  |  |  | line_reg | % | max
| FALSE | Ripple | V_in | {V_in_ripple} | I_out | {I_out_ripple} | [10 empty] | v_ripple | mV | v_ripple_% | % | max
| FALSE | Transient Response - Load Step | V_in | {V_in_transresp} | ΔIout | {dI_out_transresp} | [10 empty] | v_max_dev_ls | V | v_max_dev_ls_% | % |  | t_recovery_ls | ms |  |  | max |  |  | max
| FALSE | Transient Response - Load Dump | V_in | {V_in_transresp} | ΔIout | {dI_out_transresp} | [10 empty] | v_max_dev_ld | V | v_max_dev_ld_% | % |  | t_recovery_ld | ms |  |  | max |  |  | max
|  | Startup Overshoot | V_in | {V_in_startupovsht} | I_out | {I_out_startupovsht} | [10 empty] | v_max_dev_so | V | v_max_dev_vo_% | % | max | [11 empty] | x
|  | Hold-up Time | V_in | {V_in_t_holdup} | I_out | {I_out_t_holdup} | [10 empty] | t_holdup | ms |  |  | min
Protections | FALSE | Input Under-Voltage | I_out | {I_out_Vin_uv} | [12 empty] | v_trip_uvp | Vac |  |  | max | v_restore_uvp | Vac |  |  | max
| FALSE | Output Over-Voltage | I_out | {I_out_Vout_ov} | V_in | {V_in_Vout_ov} | [10 empty] | v_trip_ovp | V | v_trip_ovp_% | % | min/max
| FALSE | Output Overcurrent | V_in | {V_in_ocp} | [12 empty] | I_trip_ocp | A | I_trip_ocp_% | % | min/max
| FALSE | Short Circuit | V_in | {V_in_scp} | [12 empty] | scp_passfail | (none) |  |  | pass/fail
|  | Over-Temperature | V_in | {V_in_otp} | I_out | {I_out_otp} | T_amb | {T_amb_otp} | [8 empty] | T_otp | °C |  |  | min/max
Safety |  | Dielectric Withstand | DW_cond | {DW_cond} | CFG_gnd | {g_cfg_x} | [10 empty] | dw_passfail | (none) |  |  | pass/fail
|  | Output Touch Current | Lk_cond | {Lk_cond_otc} | V_in | {V_in_otc} | CFG_gnd | {g_cfg_x} | [8 empty] | I_leak_ot | uA | [10 empty] | max
|  | Earth Leakage Current | Lk_cond | {Lk_cond_elc} | V_in | {V_in_elc} | CFG_gnd | {g_cfg_x} | [8 empty] | I_leak_el | uA | [10 empty] | max
EMC |  | Conducted Emissions | CE_freq_point | {ce_freq_point} |  |  |  |  | CFG_gnd | {g_cfg_x} | V_in | {V_in_ce} | I_out | {I_out_ce} | CE_L/N | {ce_cond} | ce_av_margin | dBuV |  |  | min | ce_qp_margin | dBuV |  |  | min
|  | Radiated Emissions | RE_freq_point | {ce_freq_point} |  |  |  |  | CFG_gnd | {g_cfg_x} | V_in | {V_in_re} | I_out | {I_out_re} | RE_H/V | {re_cond} | re_pk_margin | dBuV |  |  | min | re_qp_margin | dBuV |  |  | min
|  | Electrostatic Discharge (Air) | ESD_air_loc | {location_esda} | ESD_num_strikes | {Num_strikes_esd} | ESD_voltage | {v_esd_air} | V_in | {V_in_esd} | CFG_gnd | {g_cfg_x} |  |  |  |  | esd_air_criterion | A - D | [10 empty] | min (alphabetic)
| FALSE | Electrostatic Discharge (Contact) | ESD_cnct_loc | {location_esdc} | ESD_num_strikes | {Num_strikes_esd} | ESD_voltage | {v_esd_cnct} | V_in | {V_in_esd} | CFG_gnd | {g_cfg_x} |  |  |  |  | esd_cntc_criterion | A - D | [10 empty] | min (alphabetic)
|  | EFT/Burst | EFT_input_line | {input_line_EFT} | EFT_voltage | {v_eft} |  |  | V_in | {V_in_eft} | CFG_gnd | {g_cfg_x} |  |  |  |  | eft_ctriterion | A - D | [10 empty] | min (alphabetic)
| FALSE | Lightning Surge | Surge_input_line | {input_line_surge} | Surge_voltage | {v_surge} |  |  | V_in | {V_in_surge} | CFG_gnd | {g_cfg_x} |  |  |  |  | surge_criterion | A - D | [10 empty] | min (alphabetic)

## Test Definitions (2)
|  |  | Row |  | Column (If no parameter listed, there is still a column generated with result(s) as defined in Test Result Format, but there is only one test parameter as defined in Row.) |  |  |  | Table (Generate the table as defined by Row/Column, and sweep through all combinations under Table) | [7 empty] | Row Result/Limit Format 1. A Row Calc can be created to allow calculation based on the data in a row e.g. Avg efficiency is (1/lengthEff[x]) * (Eff[1] + Eff[2] + Eff[3] + Eff[4]) or in English, the sum of each efficiency point recorded, divided by the number of points recorded
Test Category |  | Test Item | Parameter | Array | Parameter #1 | Array #1 | Parameter #2 | Array #2 | Param. #1 | Array #1 | Param. #2 | Array #2 | Param. #3 | Array #3 | Param #4 | Array #4 | Row calc result #1 Name | Row calc result #1 Unit | Row limit #1 Type | Row calc result #2 Name | Row calc result #2 Unit | Row limit #2 Type
Input | TRUE | Input Current | V_in | {V_in_I_in} | I_out | {I_out_I_in}
| TRUE | No Load Input Power | V_in | {V_in_P_nl} | I_out | {I_out_P_nl}
| FALSE | Inrush Current | V_in | {V_in_I_inrush} | I_out | {I_out_I_inrush}
| FALSE | Efficiency | V_in | {V_in_eff} | I_out | {I_out_eff} | [10 empty] | Avg Eff | % | min
| FALSE | Power Factor | V_in | {V_in_PF} | I_out | {I_out_PF}
Output | FALSE | Turn-on delay | V_in | {V_in_ton_delay} | I_out | {I_out_ton_delay}
| FALSE | Load Regulation | V_in | {V_in_loadreg} | I_out | {I_out_loadreg} | [10 empty] | load_reg | % | max
| FALSE | Line Regulation | I_out | {I_out_linereg} | V_in | {V_in_linereg} | [10 empty] | line_reg | % | max
| FALSE | Ripple | V_in | {V_in_ripple} | I_out | {I_out_ripple}
| FALSE | Transient Response - Load Step | V_in | {V_in_transresp} | ΔIout | {dI_out_transresp}
| FALSE | Transient Response - Load Dump | V_in | {V_in_transresp} | ΔIout | {dI_out_transresp}
|  | Startup Overshoot | V_in | {V_in_startupovsht} | I_out | {I_out_startupovsht} | [16 empty] | x
|  | Hold-up Time | V_in | {V_in_t_holdup} | I_out | {I_out_t_holdup}
Protections | FALSE | Input Under-Voltage | I_out | {I_out_Vin_uv}
| FALSE | Output Over-Voltage | I_out | {I_out_Vout_ov} | V_in | {V_in_Vout_ov}
| FALSE | Output Overcurrent | V_in | {V_in_ocp}
| FALSE | Short Circuit | V_in | {V_in_scp}
|  | Over-Temperature | V_in | {V_in_otp} | I_out | {I_out_otp} | T_amb | {T_amb_otp}
Safety |  | Dielectric Withstand | DW_cond | {DW_cond} | CFG_gnd | {g_cfg_x}
|  | Output Touch Current | Lk_cond | {Lk_cond_otc} | V_in | {V_in_otc} | CFG_gnd | {g_cfg_x} | [10 empty] | max
|  | Earth Leakage Current | Lk_cond | {Lk_cond_elc} | V_in | {V_in_elc} | CFG_gnd | {g_cfg_x} | [10 empty] | max
EMC |  | Conducted Emissions | CE_freq_point | {ce_freq_point} |  |  |  |  | CFG_gnd | {g_cfg_x} | V_in | {V_in_ce} | I_out | {I_out_ce} | CE_L/N | {ce_cond}
|  | Radiated Emissions | RE_freq_point | {ce_freq_point} |  |  |  |  | CFG_gnd | {g_cfg_x} | V_in | {V_in_re} | I_out | {I_out_re} | RE_H/V | {re_cond}
|  | Electrostatic Discharge (Air) | ESD_air_loc | {location_esda} | ESD_num_strikes | {Num_strikes_esd} | ESD_voltage | {v_esd_air} | V_in | {V_in_esd} | CFG_gnd | {g_cfg_x} | [6 empty] | min (alphabetic)
| FALSE | Electrostatic Discharge (Contact) | ESD_cnct_loc | {location_esdc} | ESD_num_strikes | {Num_strikes_esd} | ESD_voltage | {v_esd_cnct} | V_in | {V_in_esd} | CFG_gnd | {g_cfg_x} | [6 empty] | min (alphabetic)
|  | EFT/Burst | EFT_input_line | {input_line_EFT} | EFT_voltage | {v_eft} |  |  | V_in | {V_in_eft} | CFG_gnd | {g_cfg_x} | [6 empty] | min (alphabetic)
| FALSE | Lightning Surge | Surge_input_line | {input_line_surge} | Surge_voltage | {v_surge} |  |  | V_in | {V_in_surge} | CFG_gnd | {g_cfg_x} | [6 empty] | min (alphabetic)

## Test Arrays
Global variables/arrays (Define/set on cover sheet)
Define | Spec_low | (user defined)
Define | Nom_low | (user defined)
Define | Nom_high | (user defined)
Define | Spec_high | (user defined)
Define | {OP_num, V_out, I_out} | (user defined) |  | // If there are multiple outputs, define I_out and V_out as a 2D array (e.g. {1, 12V, 50A}, {2, 5V, 1A}, {3, 3.3V, 0.5A})
Define | {g_cfg_x} | (user defined)
Local variables/arrays (Stored in each test item)
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Define | {V_in_I_in} | 1: Spec_low; 2: Nom_low; 3: Nom_high
Define | {V_in_P_nl} | 1: Nom_low; 2: Nom_high; 3: Spec_high
Define | {V_in_I_inrush} | 1: Nom_low; 2: Nom_high; 3: Spec_high
Define | {V_in_eff} | 1: Spec_low; 2: Nom_low; 3: Nom_high
Define | {V_in_PF} | 1: Nom_low; 2: Nom_high
Define | {V_in_ton_delay} | 1: Spec_low; 2: Nom_low; 3: Nom_high
Define | {V_in_loadreg} | 1: Spec_low; 2: Spec_high
Define | {I_out_linereg} | 1: 0% * I_out; 2: 100% * I_out
Define | {V_in_ripple} | 1: Spec_low; 2: Spec_high
Define | {V_in_transresp} | 1: Spec_low; 2: Spec_high
Define | {V_in_startupovsht} | 1: Spec_low; 2: Spec_high
Define | {V_in_t_holdup} | 1: Nom_low; 2: Nom_high
Define | {I_out_Vin_uv} | 1: 100% * I_out; 2: 0% * I_out
Define | {I_out_Vout_ov} | 1: 100% * I_out; 2: 0% * I_out
Define | {V_in_ocp} | 1: Spec_low; 2: Spec_high
Define | {V_in_scp} | 1: Spec_low; 2: Spec_high
Define | {V_in_otp} | 1: Spec_low
Define | {DW_cond} | 1: "Pri-sec: 4000Vac"; 2: "Pri-earth: 1768Vac"; 3: "Sec-earth: 1500Vac"
Define | {Lk_cond_otc} | "NC (Normal)" | "NC (Rev)" | "SFC (Normal, Open Neutral)" | "SFC (Rev, Open Neutral)" | "SFC (Normal, Open Earth)" | "SFC (Rev, Open Earth)"
Define | {Lk_cond_elc} | 1: "NC (Normal)"; 2: "NC (Rev)"; 3: "SFC (Normal, Open Neutral)"; 4: "SFC (Rev, Open Neutral)"
Define | {ce_freq_point} | 1: (empty); 2: (empty); 3: (empty)
Define | {ce_freq_point} | 1: (empty); 2: (empty); 3: (empty)
Define | {location_esda} | 1: (empty); 2: (empty)
Define | {location_esdc} | 1: "HCP"; 2: "VCP"; 3: (empty); 4: (empty)
Define | {input_line_EFT} | "L" | "N" | "E" | "L+N" | "L+E" | "N+E" | "L+N+E"
Define | {input_line_surge} | 1: "L-N"; 2: "L-E"; 3: "N-E"
Define | {I_out_I_in} | 1: 100% * I_out
Define | {I_out_P_nl} | 1: 0% * I_out
Define | {I_out_I_inrush} | 1: 100% * I_out
Define | {I_out_eff} | 1: 100% * I_out; 2: 75% * I_out; 3: 50% * I_out; 4: 25% * I_out
Define | {I_out_PF} | 1: 100% * I_out; 2: 75% * I_out; 3: 50% * I_out; 4: 25% * I_out
Define | {I_out_ton_delay} | 1: 100% * I_out
Define | {I_out_loadreg} | 1: 0% * I_out; 2: 100% * I_out
Define | {V_in_linereg} | 1: Spec_low; 2: Spec_high
Define | {I_out_ripple} | 1: 100% *I_out; 2: (empty)
Define | {dI_out_transresp} | 1: 25 - 50%; 2: 50 - 75%; 3: 75 - 100%
Define | {I_out_startupovsht} | 1: 100% * I_out
Define | {I_out_t_holdup} | 1: 100% * I_out
Define | {V_in_Vout_ov} | 1: Spec_low; 2: Spec_high
Define | {I_out_otp} | 1: 100%*I_out
Define | {T_amb_otp} | 1: (empty)
Define | {V_in_otc} | 1: Spec_high
Define | {V_in_elc} | 1: Spec_high
Define | {Num_strikes_esd} | 1: 10
Define | {v_esd_air} | "+18KV" | "-18KV" | "+15KV" | "-15KV" | "+8KV" | "-8KV" | "+4KV" | "-4KV" | "+2KV" | "-2KV"
Define | {v_esd_cnct} | "+10KV" | "-10KV" | "+8KV" | "-8KV" | "+4KV | "-4KV" | "+2KV" | "-2KV"
Define | {v_eft} | "+4KV" | "-4KV" | "+2KV" | "-2KV" | "+1KV" | "-1KV"
Define | {v_surge} | "+4KV" | "-4KV" | "+2KV" | "-2KV" | "+1KV" | "-1KV"
Define | {V_in_ce} | 1: Nom_low; 2: Nom_high
Define | {I_out_ce} | 1: 50% * I_out; 2: 100% * I_out
Define | {ce_cond} | 1: "Line"; 2: "Neutral"
Define | {V_in_re} | 1: Nom_low; 2: Nom_high
Define | {I_out_re} | 1: 100% * I_out
Define | {re_cond} | 1: "Horizontal"; 2: "Vertical"
Define | {V_in_esd} | 1: (empty)
Define | {V_in_eft} | 1: (empty)
Define | {V_in_surge} | 1: (empty)

## (ex) Input Current
Cover page:
V_in | Spec_low | 90Vac
| Nom_low | 120Vac
| Nom_high | 240Vac
I_out | I_out_nom | 50A
Test sheet:
Input Current
Input Parameters
| I_out | Specification
| 50A (100%) | Input Current
V_in (Vac) | I_in (A) | (A, max)
90 | user input | user input
120 | user input | user input
240 | user input | user input
Output Current (A)
[5 empty] | 50 |  | 25
[5 empty] | Input Current (A) | c_name (units) | Input Current (A) | c_name (units) | c_name (units)
|  |  | Input Voltage (Vac) | 90 |  | f(x) |  | f(x) | f(x)
|  |  |  | 120 |  | f(x) |  | f(x) | f(x)
|  |  |  | 240 |  | f(x) |  | f(x) | f(x)
V_in (Vac) | I_out | I_in (A)
90 | 50A (100%)
120 | 50A (100%)
240 | 50A (100%)
TC1
|  |  |  | C1 | C2 | R1 | CA1 | SP1
TC2
|  |  |  | C1 | C2 | R1 | CA1 | SP1

## (ex) Efficiency
Cover page:
V_in | Spec_low | 90Vac
| Nom_low | 120Vac
| Nom_high | 240Vac
I_out | I_out_nom | 50A
Test sheet:
Efficiency
Input Parameters
| I_out |  |  |  |  | Specification
| 50A (100%) | 37.5A (75%) | 25A (50%) | 12.5A (25%) | 4-Point Efficiency | 4-Point Efficiency
V_in (Vac) | Efficiency |  |  |  | (%) | (%, min)
90 | user input | user input | user input | user input | AVG(eff1:eff4) | user input
120 | user input | user input | user input | user input | AVG(eff1:eff4) | user input
240 | user input | user input | user input | user input | AVG(eff1:eff4) | user input
C1 |  |  | \->C1
V_in (Vac) | I_out | Efficiency | 4-Point Efficiency (%) | Specification 4-point Efficiency (%, min) | P/F
90 | 50A (100%) | user input
| 37.5A (75%) | user input
| 25A (50%) | user input
| 12.5A (25%) | user input
120 | 50A (100%) | user input
| 37.5A (75%) | user input
| 25A (50%) | user input
| 12.5A (25%) | user input
240 | 50A (100%) | user input
| 37.5A (75%) | user input
| 25A (50%) | user input
| 12.5A (25%) | user input
either simple equation referencing columns, or connecting to specific condition to do an equation with all the
C1 | C2 |  | \->C1
I_out | V_in (Vac) | Efficiency | 4-Point Efficiency (%) | Specification 4-point Efficiency (%, min) | P/F
50A (100%) | 90 | user input
| 120 | user input
| 240 | user input
37.5A (75%) | 90 | user input
| 120 | user input
| 240 | user input
25A (50%) | 90 | user input
| 120 | user input
| 240 | user input
12.5A (25%) | 90 | user input
| 120 | user input
| 240 | user input

## (ex) Transient Response Step
Cover page:
V_in | Spec_low |  |  | 90Vac
| Spec_high |  |  | 264Vac
12
Test sheet:
Transient Reponse: Step Load
Input Parameters | ΔI_out
| 25 - 50% |  |  | 50 - 75% |  |  |  | 75 - 100% |  |  | Specification | Specification
|  | % Deviation |  |  | % Deviation |  |  |  | % Deviation |  | % Deviation | t_recovery
V_in | ΔV (V) | %ΔV (%) | Δt (ms) | ΔV (V) | %ΔV (%) | Δt (ms) |  | ΔV (V) | %ΔV (%) | Δt (ms) | (%ΔV, max) | (Δt, max)
90Vac | user input | f(ΔV) | user input | user input | f(ΔV) | user input |  | user input | f(ΔV) | user input | user input | user input
264Vac | user input | f(ΔV) | user input | user input | f(ΔV) | user input |  | user input | f(ΔV) | user input | user input | user input
Transient Reponse: Step Load
Input Parameters | ΔI_out | [6 empty] | ΔI_out
| 25 - 50% |  | 50 - 75% |  | 75 - 100% |  | Specification | 25 - 50% | 50 - 75% | 75 - 100% | Specification
[7 empty] | % Deviation |  |  |  | t_recovery
V_in | ΔV (V) | %ΔV (%) | ΔV (V) | %ΔV (%) | ΔV (V) | %ΔV (%) | (%ΔV, max) | Δt (ms) | Δt (ms) | Δt (ms) | (Δt, max)
90Vac | user input | f(ΔV) | user input | f(ΔV) | user input | #VALUE! | user input | user input | user input | user input | user input
264Vac | user input | f(ΔV) | user input | f(ΔV) | user input | #VALUE! | user input | user input | user input | user input | user input
Transient Reponse: Step Load
| ΔI_out | [6 empty] | ΔI_out
| 25 - 50% |  | 50 - 75% |  | 75 - 100% |  | Specification | 25 - 50% | 50 - 75% | 75 - 100% | Specification
V_in | ΔI_out | ΔV (V) | %ΔV (%) |  |  |  | % Deviation |  |  |  | t_recovery
90Vac | 25 - 50% | user input | f(ΔV) | %ΔV (%) | ΔV (V) | %ΔV (%) | (%ΔV, max) | Δt (ms) | Δt (ms) | Δt (ms) | (Δt, max)
90Vac | 50 - 75% | user input | f(ΔV) | f(ΔV) | user input | #VALUE! | user input | user input | user input | user input | user input
90Vac | 75 - 100% | user input | f(ΔV) | f(ΔV) | user input | #VALUE! | user input | user input | user input | user input | user input
V_in (Vac) | ΔI_out | ΔV (V) | %ΔV (%) | Specification % Deviation (%ΔV, max) | ΔI_out | Δt (ms) | Specification t_recovery (Δt, max) |  | V_in | ΔI_out | ΔV (V) | %ΔV (%) | Specification % Deviation (%ΔV, max) | ΔI_out | Δt (ms) | Specification t_recovery (Δt, max)
90 | 25 - 50% | user input | f(ΔV) | user input | 25 - 50% | user input | user input |  | 264Vac | 25 - 50% | user input | f(ΔV) | user input | 25 - 50% | user input | user input
90 | 50 - 75% | user input | f(ΔV) | user input | 50 - 75% | user input | user input |  | 264Vac | 50 - 75% | user input | f(ΔV) | user input | 50 - 75% | user input | user input
90 | 75 - 100% | user input | f(ΔV) | user input | 75 - 100% | user input | user input |  | 264Vac | 75 - 100% | user input | f(ΔV) | user input | 75 - 100% | user input | user input
C1 | C2 |  | #VALUE!
V_in (Vac) | ΔI_out | ΔV (V) | %ΔV (%) | Specification % Deviation (%ΔV, max) | Δt (ms) | Specification t_recovery (Δt, max)
90 | 25 - 50% | user input | f(ΔV) | user input | user input | user input
| 50 - 75% | user input | f(ΔV) | user input | user input | user input
| 75 - 100% | user input | f(ΔV) | user input | user input | user input
264Vac | 25 - 50% | user input | f(ΔV) | user input | user input | user input
| 50 - 75% | user input | f(ΔV) | user input | user input | user input
| 75 - 100% | user input | f(ΔV) | user input | user input | user input
|  |  | col_name | [5 empty] | spec_name | col_name | [5 empty] | spec_name
|  |  | col_val1 |  | col_val2 |  | col_val3 |  |  | col_val1 |  | col_val2 |  | col_val3
|  |  | result_name | calc_name | result_name | calc_name | result_name | calc_name |  | result_name | calc_name | result_name | calc_name | result_name | calc_name
| row_name | row_val1 | -- | f(x) | -- | g(x) | -- | h(x) | -- | -- | f(x) | -- | g(x) | -- | h(x) | --
| row_name | row_val2 | -- | f(x) | -- | g(x) | -- | h(x) | -- | -- | f(x) | -- | g(x) | -- | h(x) | --
| row_name | row_val3 | -- | f(x) | -- | g(x) | -- | h(x) | -- | -- | f(x) | -- | g(x) | -- | h(x) | --
|  |  | col_name |  | spec_name |  |  | spec_name |  |  | spec_name | col_name | [5 empty] | spec_name
|  |  | col_val1 |  |  | col_val2 |  |  | col_val3 |  |  | col_val1 |  | col_val2 |  | col_val3
|  |  | result_name | calc_name |  | result_name | calc_name |  | result_name | calc_name |  | result_name | calc_name | result_name | calc_name | result_name | calc_name
| row_name | row_val1 | -- | f(x) | -- | -- | g(x) | -- | -- | h(x) | -- | -- | f(x) | -- | g(x) | -- | h(x) | --
| row_name | row_val2 | -- | f(x) | -- | -- | g(x) | -- | -- | h(x) | -- | -- | f(x) | -- | g(x) | -- | h(x) | --
| row_name | row_val3 | -- | f(x) | -- | -- | g(x) | -- | -- | h(x) | -- | -- | f(x) | -- | g(x) | -- | h(x) | --
|  |  | col_name |  |  | col_name |  |  | col_name
|  |  | col_val1 |  |  | col_val2 |  |  | col_val3
|  |  | result_name |  |  | result_name |  |  | result_name
| row_name | row_val1 | -- |  |  | -- |  |  | --
| row_name | row_val2 | -- |  |  | -- |  |  | --
| row_name | row_val3 | -- |  |  | -- |  |  | --
col_name
|  |  | col_val1 |  | col_val2 |  | col_val3
|  |  | result_name | calc_name | result_name | calc_name | result_name | calc_name |  | spec_name
|  |  | -- | f(x) | -- | g(x) | -- | h(x) |  | --
|  |  | -- | f(x) | -- | g(x) | -- | h(x) |  | --
|  |  | -- | f(x) | -- | g(x) | -- | h(x) |  | --
Table Conditions
|  | row_name | col_name | result_name | calc_name | spec_name
|  | row_val1 | col_val1 | -- | g(x) | --
|  | row_val2 | col_val2 | -- | g(x) | --
|  | row_val3 | col_val3 | -- | g(x) | --

## (ex) Output Touch Current
Cover page:
V_in | Spec_high | 264Vac
110Vac
CFG_gnd | F1
F2
Test sheet:
Output Touch Current
Input Parameters | V_in = 264Vac
| CFG_gnd |  | Specification
| F1 | F2 | Output Touch Current
Lk_cond | Output Touch Current (uA) |  | (uA, max)
NC (Normal) | user input | user input | user input
NC (Rev) | user input | user input | user input
SFC (Normal, Open Neutral) | user input | user input | user input
SFC (Rev, Open Neutral) | user input | user input | user input
SFC (Normal, Open Earth) | user input | user input | user input
SFC (Rev, Open Earth) | user input | user input | user input
Output Touch Current
[5 empty] | Input Parameters | V_in = 264Vac
[7 empty] | Specification |  | Specification
[6 empty] | CFG_gnd = F1 | Output Touch Current | CFG_gnd = F2 | Output Touch Current
[5 empty] | Lk_cond | Output Touch Current (uA) | (uA, max) | Output Touch Current (uA) | (uA, max)
[5 empty] | NC (Normal) | user input | user input | user input | user input
[5 empty] | NC (Rev) | user input | user input | user input | user input
[5 empty] | SFC (Normal, Open Neutral) | user input | user input | user input | user input
[5 empty] | SFC (Rev, Open Neutral) | user input | user input | user input | user input
[5 empty] | SFC (Normal, Open Earth) | user input | user input | user input | user input
[5 empty] | SFC (Rev, Open Earth) | user input | user input | user input | user input
| CFG_GND | Lk_cond | Output Touch Current (uA) | Specification Output Touch Current (uA, max)
| F1 | NC (Normal) | user input | user input
|  | NC (Rev) | user input | user input
|  | SFC (Normal, Open Neutral) | user input | user input
|  | SFC (Rev, Open Neutral) | user input | user input
|  | SFC (Normal, Open Earth) | user input | user input
|  | SFC (Rev, Open Earth) | user input | user input
| F2 | NC (Normal) | user input | user input
|  | NC (Rev) | user input | user input
|  | SFC (Normal, Open Neutral) | user input | user input
|  | SFC (Rev, Open Neutral) | user input | user input
|  | SFC (Normal, Open Earth) | user input | user input
|  | SFC (Rev, Open Earth) | user input | user input
Note that "Limit #1 type" is not defined, but "Row limit #1 type" is defined.
This means that the limit is the same regardles of whether F1 or F2 is tested, so the specified limit is only listed once in the final column
If "Limit #1 type" was defined, then "Row limit #1 type" cannot be defined (one or the other)
If "Limit #1 type" was defined as "max", then the table would look like the below instead. (Each column gets its own limit)

## (ex) Output Touch Current (2)
Cover page:
V_in | Spec_high | 264Vac
110Vac
CFG_gnd | F1
F2
Test sheet:
Output Touch Current
Input Parameters | V_in = 264Vac
| CFG_gnd |  | Specification
| F1 | F2 | Output Touch Current
Lk_cond | Output Touch Current (uA) |  | (uA, max)
NC (Normal) | user input | user input | user input
NC (Rev) | user input | user input | user input
SFC (Normal, Open Neutral) | user input | user input | user input
SFC (Rev, Open Neutral) | user input | user input | user input
SFC (Normal, Open Earth) | user input | user input | user input
SFC (Rev, Open Earth) | user input | user input | user input
Output Touch Current V_in = 264Vac
|  |  |  | Input Parameters | CFG_gnd = F1 | Specification Output Touch Current | CFG_gnd = F2 | Specification Output Touch Current
|  |  |  | Lk_cond | Output Touch Current (uA) | (uA, max) | Output Touch Current (uA) | (uA, max)
|  |  |  | NC (Normal) | user input | user input | user input | user input
|  |  |  | NC (Rev) | user input | user input | user input | user input
|  |  |  | SFC (Normal, Open Neutral) | user input | user input | user input | user input
|  |  |  | SFC (Rev, Open Neutral) | user input | user input | user input | user input
|  |  |  | SFC (Normal, Open Earth) | user input | user input | user input | user input
|  |  |  | SFC (Rev, Open Earth) | user input | user input | user input | user input
Output Touch Current, V_in = 264Vac, CFG_gnd = F1
Input Parameters
|  |  |  | Lk_cond | Output Touch Current (uA) | Specification Output Touch Current (uA, max) | Output Touch Current (uA) | Specification Output Touch Current (uA, max)
|  |  |  | NC (Normal) | user input | user input | user input | user input
|  |  |  | NC (Rev) | user input | user input | user input | user input
|  |  |  | SFC (Normal, Open Neutral) | user input | user input | user input | user input
|  |  |  | SFC (Rev, Open Neutral) | user input | user input | user input | user input
|  |  |  | SFC (Normal, Open Earth) | user input | user input | user input | user input
|  |  |  | SFC (Rev, Open Earth) | user input | user input | user input | user input
Note that "Limit #1 type" is not defined, but "Row limit #1 type" is defined.
This means that the limit is the same regardles of whether F1 or F2 is tested, so the specified limit is only listed once in the final column
If "Limit #1 type" was defined, then "Row limit #1 type" cannot be defined (one or the other)
If "Limit #1 type" was defined as "max", then the table would look like the below instead. (Each column gets its own limit)

## (ex) Conducted Emissions
Cover page:
CFG_gnd | F1 | Grounding configurations defined on cover page
F2
Test sheet:
I_out_ce | 100% * I_out | Define output current and input voltage test conditions on the test sheet
50% * I_out
V_in_ce | 120Vac
240Vac
Constant Limit/Specification? | Yes | Limit value | 3dBuV
Conducted Emissions |  |  |  |  | Conducted Emissions |  |  |  |  | Conducted Emissions
Cfg_gnd = F1, V_in = 120Vac, I_out = 50A (100%), L/N = Line |  |  |  |  | Cfg_gnd = F1, V_in = 120Vac, I_out = 50A (100%), L/N = Neutral |  |  |  |  | Cfg_gnd = F1, V_in = 120Vac, I_out = 50A (100%), L/N = Neutral
Input Parameters |  |  |  |  | Input Parameters |  |  |  |  | Input Parameters
|  | Specification |  | Specification |  |  | Specification |  | Specification |  |  | Specification |  | Specification
|  | Average Margin |  | Quasi-Peak Margin |  |  | Average Margin |  | Quasi-Peak Margin |  |  | Average Margin |  | Quasi-Peak Margin
Frequency List | Average Margin (dBuV) | (dBuV, min) | Quasi-Peak Margin (dBuV) | (dBuV, min) | Frequency List | Average Margin (dBuV) | (dBuV, min) | Quasi-Peak Margin (dBuV) | (dBuV, min) | Frequency List | Average Margin (dBuV) | (dBuV, min) | Quasi-Peak Margin (dBuV) | (dBuV, min)
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
… | user input | 3 | user input | 3 | … | user input | 3 | user input | 3 | … | user input | 3 | user input | 3
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
Conducted Emissions |  |  |  |  | Conducted Emissions
Cfg_gnd = F1, V_in = 120Vac, I_out = 25A (50%), L/N = Line |  |  |  |  | Cfg_gnd = F1, V_in = 120Vac, I_out = 25A (50%), L/N = Neutral
Input Parameters |  |  |  |  | Input Parameters
|  | Specification |  | Specification |  |  | Specification |  | Specification
|  | Average Margin |  | Quasi-Peak Margin |  |  | Average Margin |  | Quasi-Peak Margin
Frequency List | Average Margin (dBuV) | (dBuV, min) | Quasi-Peak Margin (dBuV) | (dBuV, min) | Frequency List | Average Margin (dBuV) | (dBuV, min) | Quasi-Peak Margin (dBuV) | (dBuV, min)
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
… | user input | 3 | user input | 3 | … | user input | 3 | user input | 3
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
Conducted Emissions |  |  |  |  | Conducted Emissions
Cfg_gnd = F1, V_in = 240Vac, I_out = 50A (100%), L/N = Line |  |  |  |  | Cfg_gnd = F1, V_in = 240Vac, I_out = 50A (100%), L/N = Neutral
Input Parameters |  |  |  |  | Input Parameters
|  | Specification |  | Specification |  |  | Specification |  | Specification
|  | Average Margin |  | Quasi-Peak Margin |  |  | Average Margin |  | Quasi-Peak Margin
Frequency List | Average Margin (dBuV) | (dBuV, min) | Quasi-Peak Margin (dBuV) | (dBuV, min) | Frequency List | Average Margin (dBuV) | (dBuV, min) | Quasi-Peak Margin (dBuV) | (dBuV, min)
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
… | user input | 3 | user input | 3 | … | user input | 3 | user input | 3
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
Conducted Emissions |  |  |  |  | Conducted Emissions
Cfg_gnd = F1, V_in = 240Vac, I_out = 25A (50%), L/N = Line |  |  |  |  | Cfg_gnd = F1, V_in = 240Vac, I_out = 25A (50%), L/N = Neutral
Input Parameters |  |  |  |  | Input Parameters
|  | Specification |  | Specification |  |  | Specification |  | Specification
|  | Average Margin |  | Quasi-Peak Margin |  |  | Average Margin |  | Quasi-Peak Margin
Frequency List | Average Margin (dBuV) | (dBuV, min) | Quasi-Peak Margin (dBuV) | (dBuV, min) | Frequency List | Average Margin (dBuV) | (dBuV, min) | Quasi-Peak Margin (dBuV) | (dBuV, min)
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
… | user input | 3 | user input | 3 | … | user input | 3 | user input | 3
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
Conducted Emissions |  |  |  |  | Conducted Emissions
Cfg_gnd = F2, V_in = 120Vac, I_out = 50A (100%), L/N = Line |  |  |  |  | Cfg_gnd = F2, V_in = 120Vac, I_out = 50A (100%), L/N = Neutral
Input Parameters |  |  |  |  | Input Parameters
|  | Specification |  | Specification |  |  | Specification |  | Specification
|  | Average Margin |  | Quasi-Peak Margin |  |  | Average Margin |  | Quasi-Peak Margin
Frequency List | Average Margin (dBuV) | (dBuV, min) | Quasi-Peak Margin (dBuV) | (dBuV, min) | Frequency List | Average Margin (dBuV) | (dBuV, min) | Quasi-Peak Margin (dBuV) | (dBuV, min)
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
… | user input | 3 | user input | 3 | … | user input | 3 | user input | 3
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
Conducted Emissions |  |  |  |  | Conducted Emissions
Cfg_gnd = F2, V_in = 120Vac, I_out = 25A (50%), L/N = Line |  |  |  |  | Cfg_gnd = F2, V_in = 120Vac, I_out = 25A (50%), L/N = Neutral
Input Parameters |  |  |  |  | Input Parameters
|  | Specification |  | Specification |  |  | Specification |  | Specification
|  | Average Margin |  | Quasi-Peak Margin |  |  | Average Margin |  | Quasi-Peak Margin
Frequency List | Average Margin (dBuV) | (dBuV, min) | Quasi-Peak Margin (dBuV) | (dBuV, min) | Frequency List | Average Margin (dBuV) | (dBuV, min) | Quasi-Peak Margin (dBuV) | (dBuV, min)
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
… | user input | 3 | user input | 3 | … | user input | 3 | user input | 3
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
Conducted Emissions |  |  |  |  | Conducted Emissions
Cfg_gnd = F2, V_in = 240Vac, I_out = 50A (100%), L/N = Line |  |  |  |  | Cfg_gnd = F2, V_in = 240Vac, I_out = 50A (100%), L/N = Neutral
Input Parameters |  |  |  |  | Input Parameters
|  | Specification |  | Specification |  |  | Specification |  | Specification
|  | Average Margin |  | Quasi-Peak Margin |  |  | Average Margin |  | Quasi-Peak Margin
Frequency List | Average Margin (dBuV) | (dBuV, min) | Quasi-Peak Margin (dBuV) | (dBuV, min) | Frequency List | Average Margin (dBuV) | (dBuV, min) | Quasi-Peak Margin (dBuV) | (dBuV, min)
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
… | user input | 3 | user input | 3 | … | user input | 3 | user input | 3
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
Conducted Emissions |  |  |  |  | Conducted Emissions
Cfg_gnd = F2, V_in = 240Vac, I_out = 25A (50%), L/N = Line |  |  |  |  | Cfg_gnd = F2, V_in = 240Vac, I_out = 25A (50%), L/N = Neutral
Input Parameters |  |  |  |  | Input Parameters
|  | Specification |  | Specification |  |  | Specification |  | Specification
|  | Average Margin |  | Quasi-Peak Margin |  |  | Average Margin |  | Quasi-Peak Margin
Frequency List | Average Margin (dBuV) | (dBuV, min) | Quasi-Peak Margin (dBuV) | (dBuV, min) | Frequency List | Average Margin (dBuV) | (dBuV, min) | Quasi-Peak Margin (dBuV) | (dBuV, min)
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
… | user input | 3 | user input | 3 | … | user input | 3 | user input | 3
(user input) | user input | 3 | user input | 3 | (user input) | user input | 3 | user input | 3
This means that every row is judged against the same limit. If yes, then input the limit and it is applied to each row. If no, then each row's limit is manually user fillable.